## Notes
The Fujiclean trial at Glazebury started on 14/09/2023 and operated until 04/06/2024
The trial period consisted of a number of distinct tests:
1. Seeding & Baseline Testing
2. Hydraulic stress testing
3. Phosphorus spiking of crude
4. Storm scenario testing
The data is split across a number of spot and composite samples
The iron electrodes were switched on, on 01/11/2023
During the hydraulic stress testing, the aim was to hydraulically overload the unit to determine the operating limits of the unit
During the phosphorus spiking stage, the crude phosphorus concentration was artificially increased using sodium dihydrogen orthophosphate
During the storm scenario tests, the flow that was presented to the unit was increased over a short period of time to understand the impact of a high rate of change in flow on effluent quality
Please note the following data is included in this document
Code | Description | Units
Flow | Instantaneous flow rate at the time of sample collection | l/d
BOD | Biochemical Oxygen Demand | mg/l
COD | Chemical Oxygen Demand | mg/l
SOLI | Total Suspended Solids | mg/l
AMMO | Ammonia as N | mg/l
NTOX | Total Oxidised Nitrogen | mg/l
TONI | Total Nitrogen | mg/l
ALKA | Alkalinity | mg/l
PHOS | Total Phosphorus | mg/l
ORPH | Orthophosphate | mg/l
PH | pH | pH units
IRON | Total Iron | mg/l

## Seeding & Baseline Testing
SPOTS |  |  |  | Feed | [10 empty] | Effluent
|  |  |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l
Seeding/baseline | 1728 | 2023-09-14 | 2023-09-14 11:00 | [11 empty] | 33.6 | 150 | 51 | 32.1 | 0.32 | 39.9 | 361 | 4.47 | 3.48 | 7.71 | 0.482
Seeding/baseline | 2001.6 | 2023-11-06 | 2023-11-06 09:00 | 61 | 160 | 91 | 11 | 0.35 | 17.1 | 235 | 2.52 | 1.31 | 7.57 | 1.25
Seeding/baseline | 2001.6 | 2023-12-04 | 2023-12-04 13:00 | [11 empty] | 2 | 22 | 2.5 | 0.62 | 16.1 | 16.1 | 193 | 0.24 | 0.19 | 8.11 | 0.972
Seeding/baseline | 2001.6 | 2023-12-07 | 2023-12-07 11:15 | [5 empty] | 19.4 | 270 | 2.99 |  |  | 2.17 | [5 empty] | 12.8 | 165 | 0.2 |  |  | 0.632
Seeding/baseline | 2001.6 | 2023-12-11 | 2023-12-11 10:05 |  | 146 |  | 5.96 | 2.03 | 15.5 | 209 | 3 | 1.56 |  | 4.66 |  | 16 |  | 0.52 | 6.09 | 6.64 | 155 | 0.13 | 0.11 |  | 0.531
Seeding/baseline | 2001.6 | 2023-12-11 | 2023-12-11 10:30
Seeding/baseline | 1972.8 | 2023-12-13 | 2023-12-13 11:05 |  | 222 |  | 6.04 | 1.48 | 14.3 | 219 | 3.3 | 1.68 |  | 5.27 |  | 13 |  | 0.408 | 5.75 | 6.68 | 146 | 0.17 | 0.207 |  | 0.872
Seeding/baseline | 1972.8 | 2023-12-14 | 2023-12-14 09:10 |  | 83 |  | 8.65 | 1.58 | 14.8 | 263 | 1.6 | 1.11 |  | 1.25 |  | 17 |  | 0.69 | 6.66 | 7.85 | 149 | 0.21 | 0.19 |  | 1.05
Seeding/baseline | 1972.8 | 2023-12-18 | 2023-12-18 09:35 |  | 129 |  | 14 | 0.895 | 17.4 | 260 | 2.52 | 1.61 |  | 1.46 |  | 23 |  | 0.51 | 9.84 | 11.6 | 165 | 0.28 | 0.22 |  | 1.22
Seeding/baseline | 2001.6 | 2023-12-20 | 2023-12-20 10:35 |  | 92 |  | 11 | 0.93 | 14.7 | 263 | 1.74 | 1.2 |  | 0.891 |  | 23 |  | 0.53 | 7.2 | 8.08 | 172 | 0.24 | 0.2 |  | 0.846
Seeding/baseline | 2001.6 | 2023-12-21 | 2023-12-21 10:05 |  | 115 |  | 10.1 | 0.59 | 13.1 | 245 | 2.17 | 1.11 |  | 1.04 |  | 21 |  | 0.449 | 7.54 | 9.35 | 161 | 0.23 | 0.18 |  | 0.847
COMPS |  |  |  | Feed | [10 empty] | Effluent
|  |  |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l
Seeding/baseline | 1728 | 2023-09-14 | 2023-09-14 11:00 | 77.2 | 223 | 54 | 23.2 | 0.895 | 32.5 | 304 | 3.77 | 2.37 | 7.65 | 0.877
Seeding/baseline | 1728 | 2023-09-18 | 2023-09-18 09:00 | 154 | 343 | 193 | 25.7 | 0.895 | 37.6 | 290 | 5.43 | 3.37 | 7.55 | 1.41 | 18.5 | 64 | 18.5 | 31.7 | 0.276 | 32.8 | 326 | 3.45 | 2.91 | 8.01 | 0.418
Seeding/baseline | 1728 | 2023-09-20 | 2023-09-20 09:00 |  | 88 | 28 | 5.92 | 1.32 | 10.3 | 181 | 1.2 | 0.62 | 7.49 | 0.692 |  | 63 | 14.5 | 22.1 | 0.276 | 24.6 | 281 | 2.79 | 2.27 | 8.27 | 0.279
Seeding/baseline | 1728 | 2023-09-21 | 2023-09-21 11:00 |  | 117 | 64 | 9.15 | 0.77 | 14.8 | 212 | 2.05 | 1.03 | 7.64 | 1.07 |  | 51 | 7.5 | 18.6 | 0.45 | 20.6 | 238 | 2.6 | 1.97 | 8.23 | 0.293
Seeding/baseline | 1728 | 2023-09-25 | 2023-09-25 09:00 | 27.1 | 89 | 31 | 13.4 | 0.895 | 17.6 | 238 | 3.27 | 2.5 | 7.5 | 0.443 | 10.6 | 68 | 9.5 | 15.4 | 0.276 | 17.5 | 234 | 2.49 | 2.11 | 8.01 | 0.27
Seeding/baseline | 1728 | 2023-09-27 | 2023-09-27 09:00 | 114 | 300 | 154 | 26.9 | 0.17 | 38.6 | 361 | 4.6 | 2.93 | 7.52 | 1.11 | 10.4 | 54 | 6 | 20.4 | 0.67 | 23.4 | 285 | 2.56 | 2.28 | 8.18 | 0.24
Seeding/baseline | 1728 | 2023-09-28 | 2023-09-28 09:00 |  | 140 | 58 | 24.1 | 0.895 | 30.9 | 344 | 3.69 | 2.75 | 7.71 | 0.792 |  | 59 | 6.5 | 20.6 | 0.82 | 23.8 | 289 | 2.77 | 2.4 | 8.12 | 0.336
Seeding/baseline | 1728 | 2023-10-02 | 2023-10-02 09:00 | 39.6 | 79 | 55 | 7.07 | 0.895 | 11.7 | 210 | 1.42 | 0.78 | 7.59 | 0.676 | 13.5 | 61 | 9 | 8.93 | 7.59 | 20.5 | 213 | 2.9 | 2.48 | 7.94 | 0.189
Seeding/baseline | 1728 | 2023-10-04 | 2023-10-04 14:00 |  | 114 | 79 | 8.88 | 1.18 | 13.3 | 238 | 1.88 | 1 | 7.58 | 1.06 |  | 42 | 7 | 0.42 | 11.2 | 15.7 | 150 | 2.22 | 1.91 | 7.85 | 0.189
Seeding/baseline | 1728 | 2023-10-05 | 2023-10-05 09:00 | 54.3 | 144 | 67 | 13.9 | 0.895 | 19.7 | 349 | 2.73 | 1.61 | 7.55 | 1.07 | 2.9 | 34 | 6 | 0.48 | 9.05 | 13.5 | 151 | 1.87 | 1.75 | 7.89 | 0.151
Seeding/baseline | 2001.6 | 2023-10-09 | 2023-10-09 09:00 | 116 | 321 | 138 | 26.1 | 0.895 | 37.7 | 376 | 5.03 | 3 | 7.55 | 1.38 | 7.7 | 41 | 7.5 | 0.66 | 11.7 | 14.8 | 185 | 2.39 | 2.15 | 7.94 | 0.281
Seeding/baseline | 2001.6 | 2023-10-12 | 2023-10-12 09:00 | 40 | 305 | 218 | 14.5 | 0.895 | 23.4 | 237 | 3.77 | 2.08 | 7.45 | 1.54 | 18.8 | 52 | 8 | 0.57 | 11.9 | 13.2 | 196 | 3.04 | 2.92 | 7.9 | 0.401
Seeding/baseline | 2001.6 | 2023-10-16 | 2023-10-16 09:00 | 96.6 | 190 | 147 | 15.4 | 0.18 | 24.8 | 298 | 3.45 | 1.76 | 7.96 | 1.49 | 4 | 30 | 6.5 | 0.52 | 9.58 | 10.8 | 168 | 2.03 | 1.92 | 7.68 | 0.174
Seeding/baseline | 2001.6 | 2023-10-18 | 2023-10-18 09:00 | 89.6 | 280 | 330 | 23.1 | 0.895 | 32.6 | 369 | 4.93 | 2.92 | 7.59 | 2.79 | 3.4 | 32 | 2.5 | 0.43 | 12.6 | 13.6 | 189 | 2.11 | 1.9 | 8.05 | 0.126
Seeding/baseline | 2001.6 | 2023-10-19 | 2023-10-19 10:00 | 70.1 | 200 | 128 | 25.9 | 0.895 | 33.3 | 304 | 4.58 | 2.87 | 7.62 | 1.56 | 4.2 | 36 | 10.5 | 0.47 | 13.7 | 14.6 | 159 | 2.21 | 2.01 | 8.06 | 0.146
Seeding/baseline | 2001.6 | 2023-10-23 | 2023-10-23 09:00 | 55.1 | 87 | 58 | 8.83 | 0.96 | 14.2 | 240 | 1.82 | 0.94 | 7.55 | 1.09 | 4 | 24 | 5.5 | 0.408 | 8.65 | 9.57 | 181 | 1.48 | 1.3 | 8.13 | 0.147
Seeding/baseline | 2001.6 | 2023-10-25 | 2023-10-25 09:00 | 61.4 | 152 | 87 | 12.4 | 0.895 | 18.8 | 275 | 2.67 | 1.38 | 7.6 | 1.1 | 2.6 | 31 | 4.5 | 0.45 | 9.81 | 10.6 | 189 | 1.61 | 1.62 | 8.11 | 0.15
Seeding/baseline | 2001.6 | 2023-10-26 | 2023-10-26 09:00 | 57.2 | 132 | 100 | 17.2 | 0.895 | 22.3 | 276 | 3.12 | 1.97 | 7.6 | 1.23 | 3 | 32 | 2.5 | 0.46 | 10.7 | 11.3 | 176 | 1.6 | 1.53 | 8.07 | 0.168
Seeding/baseline | 2001.6 | 2023-10-30 | 2023-10-30 09:00 | 61.8 | 123 | 71 | 11 | 0.48 | 15.6 | 253 | 2.14 | 1.13 | 7.57 | 1.1 | 6.1 | 30 | 6.5 | 0.53 | 11.8 | 12.6 | 186 | 1.82 | 1.71 | 8.17 | 0.199
Seeding/baseline | 2001.6 | 2023-11-01 | 2023-11-01 09:00 | 45.9 | 87 | 71 | 9.84 | 0.895 | 14.4 | 271 | 1.99 | 1.06 | 7.61 | 1.96 | 3.1 | 47 | 12.5 | 0.408 | 10.3 | 12 | 176 | 1.68 | 1.56 | 8.11 | 0.277 | Electrodes Switched On
Seeding/baseline | 2001.6 | 2023-11-02 | 2023-11-02 08:00 | [11 empty] | 2 | 26 | 5 | 0.408 | 10.3 | 10.8 | 168 | 1.45 | 1.41 | 7.8 | 0.53
Seeding/baseline | 2001.6 | 2023-11-02 | 2023-11-02 08:30 | 49.5 | 107 | 89 | 9.53 | 0.895 | 14.3 | 260 | 2.29 | 1.18 | 7.6 | 1.45
Seeding/baseline | 2001.6 | 2023-11-06 | 2023-11-06 09:15 | [11 empty] | 3.4 | 28 | 7 | 0.449 | 8.74 | 9.07 | 158 | 0.55 | 0.46 | 8.16 | 1.09
Seeding/baseline | 2001.6 | 2023-11-08 | 2023-11-08 09:00 | [11 empty] | 2.1 | 23 | 3 | 0.57 | 7.42 | 7.87 | 134 | 0.46 | 0.39 | 8.16 | 1.09
Seeding/baseline | 2001.6 | 2023-11-08 | 2023-11-08 09:30 | 39.6 | 81 | 54 | 3.89 | 1.45 | 6.73 | 170 | 1.17 | 0.52 | 7.67 | 1.41
Seeding/baseline | 2001.6 | 2023-11-09 | 2023-11-09 08:15 | [11 empty] | 2.3 | 21 | 6 | 0.5 | 6.47 | 7.45 | 149 | 0.44 | 0.3 | 8.22 | 1.26
Seeding/baseline | 2001.6 | 2023-11-09 | 2023-11-09 08:30 | 32.1 | 76 | 43 | 5.73 | 1.66 | 9.42 | 217 | 1.12 | 0.58 | 7.68 | 1.02
Seeding/baseline | 2001.6 | 2023-11-13 | 2023-11-13 09:00 | 311 | 840 | 698 | 13 | 1.83 | 40.4 | 271 | 7.34 | 2.67 | 7.31 | 6.46 | 3.4 | 24 | 5 | 0.44 | 9.59 | 9.86 | 155 | 0.47 | 0.39 | 8.09 | 1.24
Seeding/baseline | 2001.6 | 2023-11-15 | 2023-11-15 09:00 | 89.3 | 157 | 181 | 9.29 | 0.895 | 16.7 | 234 | 2.5 | 1.18 | 7.5 | 2.21 | 3.2 | 26 | 12 | 0.5 | 9.26 | 10.2 | 190 | 0.46 | 0.36 | 8.09 | 1.13
Seeding/baseline | 2001.6 | 2023-11-16 | 2023-11-16 09:00 | 45 | 82 | 72 | 7.97 | 1.37 | 12.3 | 292 | 1.73 | 0.84 | 7.62 | 1.41 | 2.6 | 23 | 7 | 0.449 | 8.62 | 9.53 | 142 | 0.4 | 0.33 | 8.13 | 1.12
Seeding/baseline | 2001.6 | 2023-11-20 | 2023-11-20 09:00 | 47.5 | 107 | 69 | 5.57 | 1.01 | 10 | 203 | 1.37 | 0.65 | 7.49 | 1.2 | 1.2 | 21 | 6.5 | 0.408 | 7.61 | 8.24 | 152 | 0.34 | 0.25 | 8.1 | 0.876
Seeding/baseline | 2001.6 | 2023-11-22 | 2023-11-22 09:00 | 77.1 | 223 | 168 | 14 | 0.895 | 21.2 | 264 | 2.95 | 1.67 | 7.55 | 1.88 | 3 | 24 | 5 | 0.408 | 7.87 | 9.02 | 158 | 0.41 | 0.32 | 8.12 | 1.03
Seeding/baseline | 2001.6 | 2023-11-23 | 2023-11-23 09:00 | 78 | 253 | 188 | 16.5 | 0.29 | 25.6 | 278 | 3.86 | 2.18 | 7.53 | 2.82 | 1.9 | 24 | 7.5 | 0.408 | 9.9 | 10.4 | 171 | 0.41 | 0.31 | 8.13 | 0.952
Seeding/baseline | 2001.6 | 2023-11-27 | 2023-11-27 09:00 | 199 | 526 | 418 | 24.4 | 0.895 | 39.4 | 307 | 6.34 | 3.62 | 7.42 | 4.73 | 4.9 | 68 | 17.5 | 0.87 | 13.3 | 14.6 | 196 | 0.74 | 0.52 | 8.03 | 1.36
Seeding/baseline | 2001.6 | 2023-11-29 | 2023-11-29 09:00 | 85.5 | 270 | 150 | 17.4 | 0.895 | 23.7 | 294 | 3.63 | 1.93 | 7.68 | 2.06 | 3.2 | 34 | 8.5 | 0.408 | 11.9 | 12.6 | 179 | 0.39 | 0.29 | 8.18 | 1.04
Seeding/baseline | 2001.6 | 2023-11-30 | 2023-11-30 09:00 | 101 | 215 | 302 | 20.8 | 0.895 | 31.3 | 315 | 4.2 | 2.53 | 7.64 | 2.65 | 2 | 49 | 4 | 0.408 | 12.4 | 13.1 | 174 | 0.33 | 0.24 | 8.05 | 0.771
Seeding/baseline | 2001.6 | 2023-12-04 | 2023-12-04 08:00 | 279 | 802 | 1270 | 19.2 | 0.895 | 51.2 | 287 | 9.51 | 4.52 | 7.58 | 10.9 | 2.9 | 26 | 3.5 | 0.84 | 17 | 17.4 | 190 | 0.31 | 0.24 | 8.09 | 0.934
Seeding/baseline | 2001.6 | 2023-12-06 | 2023-12-06 09:00 |  | 171 | 218 | 7.21 | 1.69 | 13.6 | 230 | 2.38 | 1.3 | 7.58 | 2.15 |  | 22 | 6 | 0.86 | 12.5 | 13.3 | 174 | 0.2 | 0.19 | 8.12 | 0.831
Seeding/baseline | 2001.6 | 2023-12-07 | 2023-12-07 09:00 | 70.3 | 204 | 131 | 16.2 | 1.48 | 7.45 | 277 | 2.97 | 1.8 | 7.55 | 1.54 | 1.6 | 18 | 6 | 0.97 | 11.8 | 12.6 | 165 | 0.22 | 0.207 | 8.06 | 0.739
Seeding/baseline | 2001.6 | 2023-12-11 | 2023-12-11 09:00 | 39.6 | 60 | 46 | 5.19 | 1.22 | 9.68 | 172 | 1.6 | 1.12 | 7.51 | 0.979 | 1.5 | 20 | 5 | 0.56 | 6.08 | 6.92 | 132 | 0.18 | 0.14 | 8.08 | 0.625
Seeding/baseline | 1972.8 | 2023-12-13 | 2023-12-13 09:00 | 24.5 | 62 | 45 | 6.12 | 1.73 | 11 | 196 | 1.14 | 0.73 | 7.64 | 0.856 | 1.8 | 14 | 8.5 | 0.408 | 5.94 | 6.78 | 158 | 0.19 | 0.207 | 8.11 | 0.963
Seeding/baseline | 1972.8 | 2023-12-14 | 2023-12-14 09:00 | 55.2 | 112 | 84 | 11.1 | 0.98 | 16.4 | 250 | 1.95 | 1.31 | 7.19 | 1.34 | 2.3 | 24 | 4 | 0.61 | 6.15 | 6.73 | 131 | 0.2 | 0.17 | 8.01 | 0.902
Seeding/baseline | 1972.8 | 2023-12-18 | 2023-12-18 09:00 | 87 | 203 | 93 | 19.4 | 0.895 | 29.7 | 298 | 3.66 | 2.13 | 7.44 | 1.06 | 3.3 | 26 | 9 | 0.57 | 9.82 | 11.5 | 177 | 0.36 | 0.25 | 7.96 | 1.31
Seeding/baseline | 2001.6 | 2023-12-20 | 2023-12-20 09:00 | 84.4 | 207 | 112 | 13.7 | 0.895 | 22.4 | 239 | 2.8 | 1.62 | 7.35 | 1.22 | 1.8 | 22 | 5.5 | 0.49 | 8.03 | 8.93 | 177 | 0.31 | 0.22 | 7.97 | 0.987
Seeding/baseline | 2001.6 | 2023-12-21 | 2023-12-21 09:00 | 68.2 | 193 | 95 | 15.5 | 0.28 | 23.1 | 265 | 2.94 | 1.67 | 7.44 | 1.01 | 2.1 | 26 | 8 | 0.449 | 7.68 | 8.68 | 164 | 0.3 | 0.22 | 8.02 | 1.04

## Hydraulic Stress Testing
SPOTS |  |  |  | Feed | [10 empty] | Effluent
|  | Date |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | Notes
Hydraulic Stress testing | 2952 | 2024-01-04 | 2024-01-04 11:30 |  | 138 |  | 9.74 | 1.61 | 18.9 | 251 | 2.18 | 1.78 |  | 0.855 |  | 17 |  | 0.408 | 4.45 | 5.27 | 126 | 0.24 | 0.207 |  | 0.467
Hydraulic Stress testing | 2952 | 2024-01-08 | 2024-01-08 10:30 |  | 466 |  | 15.4 | 1.79 | 29.3 | 265 | 6.15 | 3.48 |  | 8.84 |  | 27 |  | 0.88 | 10.2 | 12.4 | 189 | 0.48 | 0.35 |  | 0.903
Hydraulic Stress testing | 2966.4 | 2024-01-10 | 2024-01-10 10:30 |  | 445 |  | 22.2 | 1.62 | 39.8 | 303 | 5.09 | 3.04 |  | 2.82 |  | 38 |  | 1.31 | 8.59 | 11.2 | 244 | 0.5 | 0.44 |  | 1.07
Hydraulic Stress testing | 2966.4 | 2024-01-12 | 2024-01-12 11:05 |  | 279 |  | 21.7 | 1.6 | 32 | 304 | 4.88 | 3.12 |  | 4.54 |  | 40 |  | 4.84 | 11 | 16.4 | 222 | 0.7 | 0.5 |  | 1.09
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:01 | [12 empty] | 44 |  | 15.1 | 4.06 | 19.8 | 286 | 0.77 | 0.59 |  | 1.81
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:30 |  | 285 |  | 36.4 | 1.59 | 46 | 358 | 5.48 | 3.8 |  | 1.3 |  | 45 |  | 14.7 | 4.48 | 19.4 | 294 | 0.95 | 0.7 |  | 1.96
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:31
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:32 |  | 249 |  | 19.5 | 1.73 | 29.3 | 259 | 3.83 | 2.52 |  | 2.5
Hydraulic Stress testing | 3009.6 | 2024-01-23 | 2024-01-23 10:30 |  | 262 |  | 27.2 | 1.63 | 39.6 | 328 | 3.54 | 3.4 |  | 1.29
Hydraulic Stress testing | 3009.6 | 2024-01-23 | 2024-01-23 11:00 | [12 empty] | 33 |  | 3.23 | 9.69 | 13.8 | 204 | 0.53 | 0.35 |  | 1.08
Hydraulic Stress testing | 3009.6 | 2024-01-24 | 2024-01-24 10:30 |  | 240 |  | 14.6 | 1.63 | 23.6 | 265 | 3.24 | 2.14 |  | 2.42 |  | 30 |  | 2.47 | 10.9 | 14.1 | 197 | 0.52 | 0.44 |  | 1.27
Hydraulic Stress testing | 3009.6 | 2024-01-25 | 2024-01-25 09:05 |  | 145 |  | 13.6 | 1.78 | 19.5 | 251 | 2.6 | 1.67 |  | 1.29 |  | 25 |  | 3.8 | 7.15 | 11.4 | 194 | 0.46 | 0.33 |  | 1.16
Hydraulic Stress testing | 3009.6 | 2024-01-30 | 2024-01-30 09:30 |  | 252 |  | 24.6 | 1.42 | 38.5 | 327 | 4.85 | 3.24 |  | 2.21 |  | 26 |  | 0.41 | 6.99 | 8.19 | 180 | 0.28 | 0.29 |  | 0.606
Hydraulic Stress testing | 3009.6 | 2024-01-31 | 2024-01-31 09:30 |  | 205 |  | 12.6 | 1.88 | 17.9 | 283 | 2.11 | 1.51 |  | 1.3 |  | 24 |  | 1.35 | 6.88 | 8.86 | 168 | 0.31 | 0.38 |  | 0.706
Hydraulic Stress testing | 3009.6 | 2024-02-01 | 2024-02-01 09:30 |  | 158 |  | 14.2 | 1.68 | 17.1 | 238 | 2.74 | 1.84 |  | 2.27 |  | 22 |  | 0.75 | 7.17 | 8.16 | 155 | 0.24 | 0.12 |  | 0.568
Hydraulic Stress testing | 3009.6 | 2024-02-05 | 2024-02-05 09:10 | 32.1 | 78 | 29 | 14.1 | 1.95 | 18.4 | 301 | 2.07 | 1.52 | 7.75 | 1.01 | 2.6 | 25 | 5.5 | 1.56 | 7.31 | 8.26 | 200 | 0.33 | 0.24 | 7.79 | 0.553
Hydraulic Stress testing | 3009.6 | 2024-02-07 | 2024-02-07 10:30 | [12 empty] | 18 |  | 0.42 | 5.91 | 6.67 | 191 | 0.26 | 0.22 |  | 0.588
Hydraulic Stress testing | 3009.6 | 2024-02-07 | 2024-02-07 10:45 |  | 358 |  | 7.59 | 1.64 | 19 | 227 | 3.56 | 1.5 |  | 4.07
Hydraulic Stress testing | 3009.6 | 2024-02-08 | 2024-02-08 10:00 |  | 155 |  | 12.3 | 1.55 | 22.1 | 296 | 3.14 | 1.92 |  | 3.44 |  | 22 |  | 0.77 | 6.57 | 7.81 | 215 | 0.27 | 0.26 |  | 0.884
Hydraulic Stress testing | 3009.6 | 2024-02-08 | 2024-02-08 10:01
Hydraulic Stress testing | 3168 | 2024-02-12 | 2024-02-12 08:10 | 45 | 67 | 25.82 | 11 | 2.47 | 16.1 | 280 | 1.47 | 1.29 | 7.77 | 0.843 | 1.4 | 21 | 2.5 | 0.59 | 8.91 | 9.44 | 185 | 0.18 | 0.19 | 7.69 | 0.605
Hydraulic Stress testing | 3168 | 2024-02-14 | 2024-02-14 11:30 |  | 258 |  | 30.5 | 1.17 | 40.8 | 272 | 4.89 | 3.75 |  | 1.69 |  | 25 |  | 0.85 | 10.4 | 10.7 | 214 | 0.19 | 0.21 |  | 0.534
Hydraulic Stress testing | 3499.2 | 2024-02-15 | 2024-02-15 09:30 | 148 | 365 | 280 | 8.1 | 1.22 | 18.4 | 189 | 3.36 | 1.56 | 7.25 | 2.99 | 1.9 | 18 | 2 | 0.41 | 6.84 | 7.62 | 200 | 0.25 | 0.19 | 7.46 | 0.561
Hydraulic Stress testing | 3499.2 | 2024-02-19 | 2024-02-19 13:30 | 128 | 353 | 248 | 12.4 | 1.27 | 23 | 220 | 4.04 | 1.94 | 7.53 | 3.37 | 1.9 | 18 | 3 | 0.53 | 3.35 | 3.9 | 161 | 0.29 | 0.24 | 7.99 | 0.687
Hydraulic Stress testing | 3744 | 2024-02-21 | 2024-02-21 10:20 | [11 empty] | 2 | 24 | 3.5 | 0.67 | 5.42 | 6.25 | 155 | 0.29 | 0.19 | 7.64 | 0.804
Hydraulic Stress testing | 3744 | 2024-02-21 | 2024-02-21 10:30 | 32.8 | 130 | 89 | 5.17 | 1.48 | 9.45 | 126 | 1.45 | 0.91 | 7.57 | 2.23
Hydraulic Stress testing | 3744 | 2024-02-22 | 2024-02-22 14:00 | 32.1 | 69 | 48 | 1.95 | 1.68 | 5.4 | 107 | 0.73 | 0.48 | 7.55 | 1.64 | 1.9 | 8.8 | 4 | 0.71 | 3.5 | 4.11 | 136 | 0.24 | 0.207 | 7.77 | 0.679
Hydraulic Stress testing | 3744 | 2024-02-26 | 2024-02-26 14:00 | 114 | 303 | 80 | 25.1 | 0.7 | 35.9 | 295 | 4.59 | 3.28 | 7.92 | 1.33 | 2.7 | 19 | 6.5 | 0.9 | 7.18 | 8.3 | 156 | 0.28 | 0.24 | 7.62 | 0.776
Hydraulic Stress testing | 3744 | 2024-02-28 | 2024-02-28 11:15 | 74.3 | 193 | 106 | 30.7 | 1.9 | 39.2 | 299 | 4.77 | 3.48 | 7.89 | 1.7
Hydraulic Stress testing | 3744 | 2024-02-28 | 2024-02-28 11:30 | [11 empty] | 1.8 | 49 | 7 | 0.87 | 9.19 | 10 | 155 | 0.64 | 0.88 | 7.61 | 2.23
Hydraulic Stress testing | 3998.88 | 2024-02-29 | 2024-02-29 10:00 | [11 empty] | 1.8 | 21 | 3.5 | 0.88 | 8.29 | 9.18 | 129 | 0.18 | 0.179 | 7.6 | 0.433
Hydraulic Stress testing | 3998.88 | 2024-02-29 | 2024-02-29 10:15 | 56.8 | 159 | 88 | 18 | 1.47 | 26.6 | 220 | 3.25 | 2.17 | 7.6 | 2.14
Hydraulic Stress testing | 3600 | 2024-03-04 | 2024-03-04 14:00 | 109 | 316 | 125 | 27.4 | 1.88 | 37.2 | 278 | 4.64 | 3.39 | 7.46 | 1.22 | 1.8 | 17 | 3 | 0.92 | 4.8 | 5.47 | 156 | 0.19 | 0.25 | 7.9 | 0.508
Hydraulic Stress testing | 3998.88 | 2024-03-06 | 2024-03-06 12:30 | [12 empty] | 20 | 5.5 | 0.51 | 12.7 | 13.9 | 138 | 0.27 | 0.24 | 7.75 | 0.879
Hydraulic Stress testing | 3998.88 | 2024-03-06 | 2024-03-06 12:45 | 135 | 325 | 117 | 42.4 | 2.41 | 58.1 | 351 | 6.21 | 4.88 | 7.88 | 1.18
Hydraulic Stress testing | 4032 | 2024-03-07 | 2024-03-07 10:30 | 153 | 361 | 170 | 39.6 | 0.9 | 50 | 322 | 7.49 | 4.8 | 7.59 | 1.77
Hydraulic Stress testing | 4032 | 2024-03-07 | 2024-03-07 10:45 | [11 empty] | 6.4 | 37 | 5.5 | 3.09 | 10.6 |  |  | 0.5 | 0.41 | 7.55 | 1.29
Hydraulic Stress testing | 4032 | 2024-03-07 | 2024-03-07 11:00
Hydraulic Stress testing | 3960 | 2024-03-11 | 2024-03-11 14:00 | 143 | 380 | 180 | 29.2 | 1.83 | 39.4 | 292 | 4.92 | 3.67 | 7.65 | 2.11 | 1.8 | 20 | 2.5 | 0.408 | 9.71 | 11.4 | 140 | 0.25 | 0.207 | 7.59 | 0.679
Hydraulic Stress testing | 3960 | 2024-03-13 | 2024-03-13 08:30 | [11 empty] | 2.2 | 23 | 1.5 | 0.82 | 7.65 | 8.81 | 148 | 0.25 | 0.18 | 7.52 | 0.948
Hydraulic Stress testing | 3960 | 2024-03-13 | 2024-03-13 08:40 | 59.4 | 165 | 77 | 20.4 | 1.9 | 33.8 | 286 | 3.75 | 2.95 | 7.75 | 1.27
Hydraulic Stress testing | 3960 | 2024-03-14 | 2024-03-14 09:45 | 45.6 | 145 | 130 | 16.8 | 1.85 | 27.7 | 263 | 3.51 | 2.44 | 7.57 | 1.62
Hydraulic Stress testing | 3960 | 2024-03-14 | 2024-03-14 09:50 | [11 empty] | 1.8 | 20 | 2.5 | 0.58 | 8.63 | 9.52 | 130 | 0.24 | 0.179 | 7.41 | 0.537
Hydraulic Stress testing | 3960 | 2024-03-18 | 2024-03-18 13:30 | 28 | 315 | 53 | 26.1 | 1.6 | 40.1 | 268 | 4.59 | 3.26 | 7.36 | 1.07 | 1.8 | 20 | 5 | 0.78 | 7.2 | 8.6 | 149 | 0.32 | 0.24 | 7.63 | 1.15
Hydraulic Stress testing | 4248 | 2024-03-20 | 2024-03-20 10:50 |  | 125 | 96 | 6.17 | 1.06 | 11.5 | 162 | 1.64 | 1.06 | 7.33 | 1.21 |  | 27 | 6 | 3.83 | 5.3 | 9.87 | 133 | 0.39 | 0.3 | 7.72 | 1.5
Hydraulic Stress testing | 4248 | 2024-03-21 | 2024-03-21 12:30 | 90.7 | 231 | 105 | 20 | 1.11 | 29.4 | 289 | 3.41 | 2.86 | 7.4 | 0.999
Hydraulic Stress testing | 4248 | 2024-03-21 | 2024-03-21 12:40 | [11 empty] | 3.1 | 19 | 3.5 | 1.28 | 5.01 | 6.69 | 161 | 0.33 | 0.26 | 7.57 | 1.27
Hydraulic Stress testing | 4248 | 2024-03-25 | 2024-03-25 11:10 | 72.3 | 265 | 187 | 14.6 | 0.895 | 22.4 | 205 | 3.07 | 1.82 | 7.57 | 2.87
Hydraulic Stress testing | 4248 | 2024-03-25 | 2024-03-25 11:15 | [11 empty] | 4.1 | 31 | 6 | 6.86 | 3.4 | 11.5 | 128 | 0.51 | 0.37 | 7.54 | 1.44
Hydraulic Stress testing | 4752 | 2024-03-27 | 2024-03-27 10:30 | 68.2 | 177 | 81 | 16.7 | 1.53 | 25 | 235 | 3.2 | 2.15 | 7.64 | 2.08
Hydraulic Stress testing | 4752 | 2024-03-27 | 2024-03-27 11:00 | [11 empty] | 2.6 | 24 | 7.5 | 6.08 | 4.55 | 11.1 | 162 | 0.42 | 0.35 | 7.98 | 1.12
Hydraulic Stress testing | 4752 | 2024-03-27 | 2024-03-27 11:05
Hydraulic Stress testing | 4752 | 2024-03-28 | 2024-03-28 08:15 | 46.6 | 68 | 56 | 5.42 | 1.41 | 8.87 | 187 | 1.21 | 0.71 | 7.51 | 2.22
Hydraulic Stress testing | 4752 | 2024-03-28 | 2024-03-28 08:30 | [11 empty] | 2.3 | 21 | 6 | 4.53 | 3.43 | 8.73 | 143 | 0.42 | 0.32 | 7.5 | 1.69
COMPS |  |  |  | Feed | [10 empty] | Effluent
|  |  |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | Notes
Hydraulic Stress testing | 3009.6 | 2024-01-02 | 2024-01-02 09:00 | 60.9 | 175 | 291 | 5.47 | 1.08 | 12.4 | 184 | 4.57 | 0.86 | 7.4 | 4.44 | 2.3 | 21 | 17 | 0.408 | 5.78 | 6.45 | 157 | 0.57 | 0.6 | 8.02 | 2.04
Hydraulic Stress testing | 2952 | 2024-01-03 | 2024-01-03 09:00 | 62.1 | 157 | 144 | 3.04 | 1.18 | 8.83 | 137 | 1.4 | 0.65 | 7.49 | 2.18 | 2.4 | 23 | 9 | 0.408 | 4.33 | 4.81 | 122 | 0.42 | 0.31 | 8.09 | 1.44
Hydraulic Stress testing | 2952 | 2024-01-04 | 2024-01-04 09:00 | 45 | 86 | 57 | 6.91 | 0.91 | 12.3 | 209 | 1.29 | 0.86 | 7.71 | 1.18 | 2.3 | 21 | 13 | 0.408 | 4.17 | 4.94 | 168 | 0.51 | 0.49 | 8.12 | 1.94
Hydraulic Stress testing | 2952 | 2024-01-08 | 2024-01-08 09:00 | 73 | 191 | 99 | 19.1 | 0.895 | 25.2 | 283 | 3.19 | 2.05 | 7.5 | 1.03 | 5 | 38 | 22.5 | 0.66 | 9.67 | 12.1 | 200 | 0.87 | 0.61 | 7.84 | 2.88
Hydraulic Stress testing | 2966.4 | 2024-01-10 | 2024-01-10 09:00 | 174 | 405 | 282 | 22.5 | 0.895 | 37.9 | 311 | 4.67 | 2.85 | 7.48 | 2.61 | 8.6 | 34 | 13 | 1.1 | 9.65 | 10.5 | 208 | 0.5 | 0.41 | 7.84 | 0.982
Hydraulic Stress testing | 2966.4 | 2024-01-12 | 2024-01-12 09:00 | 95.2 | 234 | 117 | 25.1 | 0.895 | 35.9 | 352 | 4.24 | 2.76 | 7.6 | 1.13 | 6 | 36 | 8 | 3.14 | 11.7 | 15.8 | 186 | 0.67 | 0.51 | 7.94 | 1.08
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:00 | 127 | 328 | 163 | 36.4 | 1.33 | 46.6 | 396 | 5.75 | 3.87 | 7.78 | 1.47 | 7.7 | 45 | 10.5 | 14.3 | 3.92 | 6.62 | 277 | 0.96 | 0.68 | 8.03 | 1.86
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:31 | 170 | 574 | 338 | 24.5 | 1.79 | 38.4 | 290 | 5.49 | 3.3 | 7.57 | 2.55
Hydraulic Stress testing | 3009.6 | 2024-01-16 | 2024-01-16 09:32 | [11 empty] | 7.4 | 42 | 12.5 | 15.3 | 4.58 | 20.9 | 285 | 0.85 | 0.69 | 8.1 | 2.03
Hydraulic Stress testing | 3009.6 | 2024-01-23 | 2024-01-23 09:00 | 107 | 264 | 241 | 18.3 | 0.895 | 28.8 | 286 | 3.37 | 1.98 | 7.61 | 1.59
Hydraulic Stress testing | 3009.6 | 2024-01-24 | 2024-01-24 10:00 |  | 345 | 254 | 23.6 | 0.895 | 34.4 | 279 | 4.27 | 3.14 | 7.8 | 2.17 |  | 48 | 18.5 | 3.71 | 9.92 | 15.7 | 201 | 1.79 | 1 | 8 | 6.4
Hydraulic Stress testing | 3009.6 | 2024-01-25 | 2024-01-25 09:00 |  | 181 | 100 | 16.8 | 0.91 | 24.3 | 274 | 3.24 | 1.78 | 7.57 | 1.38 |  | 29 | 7 | 3.08 | 8.95 | 12.6 | 198 | 0.52 | 0.38 | 7.98 | 1.25
Hydraulic Stress testing | 3009.6 | 2024-01-30 | 2024-01-30 09:00 | 79.5 | 177 | 144 | 16.1 | 0.895 | 23.4 | 237 | 3.25 | 2.18 | 7.57 | 1.53 | 2.7 | 30 | 9 | 0.46 | 7.68 | 8.67 | 183 | 0.41 | 0.31 | 7.98 | 1.09
Hydraulic Stress testing | 3009.6 | 2024-01-31 | 2024-01-31 09:00 | 62.1 | 187 | 110 | 16.2 | 0.895 | 23 | 281 | 2.59 | 1.78 | 7.56 | 1.06 | 2.8 | 21 | 4 | 0.96 | 6.95 | 8.35 | 166 | 0.35 | 0.41 | 8 | 0.805
Hydraulic Stress testing | 3009.6 | 2024-02-01 | 2024-02-01 09:00 |  | 187 | 130 | 14.1 | 0.91 | 19.3 | 226 | 2.54 | 1.62 | 7.53 | 1.41 |  | 24 | 3.5 | 1.3 | 7.96 | 9.43 | 178 | 0.33 | 0.13 | 7.88 | 0.712
Hydraulic Stress testing | 3009.6 | 2024-02-05 | 2024-02-05 09:00 | 116 | 284 | 144 | 20.7 | 0.34 | 31 | 329 | 4.01 | 2.51 | 7.65 | 2.08 | 3.5 | 37 | 11.5 | 1.51 | 7.58 | 9.08 | 202 | 0.56 | 0.51 | 7.86 | 1.36
Hydraulic Stress testing | 3009.6 | 2024-02-07 | 2024-02-07 10:00 | 65 | 173 | 235 | 11.1 | 1.07 | 16.3 | 210 | 2.81 | 1.47 | 7.33 | 2.08 | 2 | 26 | 4 | 0.55 | 7.66 | 8.48 | 214 | 0.36 | 0.32 | 7.99 | 0.754
Hydraulic Stress testing | 3009.6 | 2024-02-08 | 2024-02-08 09:00 | 53.8 | 151 | 92 | 16.6 | 0.68 | 21.9 | 301 | 2.48 | 1.64 | 7.61 | 1.08
Hydraulic Stress testing | 3009.6 | 2024-02-08 | 2024-02-08 09:01 | [11 empty] | 3.2 | 43 | 6 | 0.81 | 5.79 | 7.23 | 227 | 0.38 | 0.35 | 7.74 | 0.914
Hydraulic Stress testing | 3168 | 2024-02-12 | 2024-02-12 08:00 | 51.2 | 165 | 74 | 17.3 | 1.14 | 24 | 293 | 2.7 | 1.83 | 7.63 | 1.1 | 2.1 | 20 | 4.5 | 0.6 | 8.6 | 9.19 | 177 | 0.28 | 0.18 | 7.97 | 0.762
Hydraulic Stress testing | 3168 | 2024-02-14 | 2024-02-14 11:00 | 72.4 | 181 | 82 | 20.1 | 0.25 | 26.8 | 312 | 3.41 | 2.19 | 7.52 | 1.33 | 1.9 | 24 | 3.5 | 1.07 | 10.5 | 11.5 | 220 | 0.28 | 0.21 | 7.67 | 0.778
Hydraulic Stress testing | 3499.2 | 2024-02-15 | 2024-02-15 10:00 | 273 | 594 | 459 | 13.9 | 1.79 | 28.6 | 200 | 5.55 | 2.54 | 7.2 | 3.88 | 1.9 | 21 | 3 | 0.408 | 8.85 | 9.48 | 198 | 0.27 | 0.21 | 7.61 | 0.706
Hydraulic Stress testing | 3499.2 | 2024-02-19 | 2024-02-19 09:00 | 80.4 | 188 | 163 | 7.31 | 0.895 | 14.2 | 205 | 3.06 | 1.29 | 7.61 | 2.74 | 1.9 | 27 | 3.5 | 0.408 | 3.66 | 4.22 | 152 | 0.32 | 0.23 | 7.86 | 0.829
Hydraulic Stress testing | 3744 | 2024-02-21 | 2024-02-21 09:00 | 59.1 | 176 | 93 | 12.3 | 0.94 | 17.3 | 216 | 2.37 | 1.39 | 7.48 | 1.27 | 1.9 | 21 | 2.5 | 0.62 | 6.1 | 6.56 | 160 | 0.27 | 0.2 | 7.4 | 0.582
Hydraulic Stress testing | 3744 | 2024-02-22 | 2024-02-22 09:00 | 32.3 | 95 | 69 | 4.79 | 1.32 | 9.41 | 122 | 1.16 | 0.68 | 7.5 | 1.29 | 1.9 | 12 | 1.74 | 0.69 | 4.41 | 5.03 | 79 | 0.23 | 0.207 | 7.91 | 0.502
Hydraulic Stress testing | 3744 | 2024-02-26 | 2024-02-26 09:00 | 62.8 | 187 | 45 | 16.6 | 0.52 | 21.3 | 255 | 2.73 | 1.85 | 7.55 | 1.13 | 3 | 19 | 4 | 0.74 | 7.23 | 8.22 | 160 | 0.25 | 0.19 | 7.69 | 0.578
Hydraulic Stress testing | 3744 | 2024-02-28 | 2024-02-28 11:00 | 71.8 | 207 | 105 | 20.7 | 0.895 | 27.3 | 260 | 3.49 | 2.26 | 7.7 | 1.4 | 1.9 | 23 | 3 | 1.17 | 9.98 | 11 | 164 | 0.29 | 0.23 | 7.54 | 0.582
Hydraulic Stress testing | 3998.88 | 2024-02-29 | 2024-02-29 10:30 | 82 | 220 | 119 | 16.8 | 0.7 | 26.4 | 212 | 3.71 | 2.08 | 7.51 | 2.28 | 1.8 | 21 | 4.5 | 0.82 | 9.97 | 11.2 | 134 | 0.23 | 0.179 | 7.73 | 0.464
Hydraulic Stress testing | 3600 | 2024-03-04 | 2024-03-04 09:00 | [11 empty] | 2.1 | 15 | 6 | 0.76 | 6.13 | 6.91 | 151 | 0.18 | 0.21 | 7.86 | 0.34
Hydraulic Stress testing | 3998.88 | 2024-03-06 | 2024-03-06 12:00 | 7.2 | 214 | 106 | 23.5 | 1.06 | 32 | 273 | 3.9 | 2.57 | 7.65 | 1.23 | 3.9 | 22 | 11 | 0.78 | 11.7 | 13.3 | 142 | 0.37 | 0.29 | 7.54 | 0.981
Hydraulic Stress testing | 4032 | 2024-03-07 | 2024-03-07 10:00 | 106 | 317 | 164 | 26.8 | 0.895 | 38.5 | 272 | 5.52 | 3.08 | 7.43 | 1.43
Hydraulic Stress testing | 4032 | 2024-03-07 | 2024-03-07 10:15 | [11 empty] | 5.5 | 52 | 4.5 | 2.75 | 11.9 |  |  | 0.55 | 0.37 | 7.56 | 1.41
Hydraulic Stress testing | 3960 | 2024-03-11 | 2024-03-11 09:00 | 138 | 327 | 110 | 27.9 | 0.895 | 35 | 307 | 7.59 | 6.3 | 7.47 | 1.2 | 2.4 | 24 | 7 | 0.408 | 13.2 | 14.7 | 122 | 0.31 | 0.21 | 7.7 | 0.566
Hydraulic Stress testing | 3960 | 2024-03-13 | 2024-03-13 08:00 | 56.2 | 149 | 89 | 10.2 | 1.5 | 15.4 | 198 | 2.18 | 1.21 | 7.55 | 1.47 | 3.9 | 27 | 8.5 | 0.86 | 9.55 | 10.9 | 141 | 0.46 | 0.25 | 7.5 | 1.82
Hydraulic Stress testing | 3960 | 2024-03-14 | 2024-03-14 10:00 | 73.1 | 253 | 142 | 13.6 | 0.29 | 22.1 | 233 | 3.52 | 2.11 | 7.46 | 2.06 | 1.8 | 23 | 4 | 0.7 | 8.8 | 9.95 | 135 | 0.41 | 0.24 | 7.3 | 1.27
Hydraulic Stress testing | 3960 | 2024-03-18 | 2024-03-18 09:00 | 62.4 | 169 | 62 | 14.9 | 0.59 | 22.1 | 237 | 2.65 | 1.65 | 7.49 | 0.949 | 2.5 | 29 | 15.5 | 0.75 | 7.52 | 8.99 | 114 | 0.57 | 0.43 | 7.58 | 2.06
Hydraulic Stress testing | 4248 | 2024-03-20 | 2024-03-20 09:00 |  | 241 | 141 | 15.5 | 0.895 | 24.4 | 219 | 3.39 | 1.98 | 7.31 | 1.57 |  | 27 | 4 | 4.02 | 6.33 | 11.3 | 151 | 0.43 | 0.38 | 7.65 | 1.31
Hydraulic Stress testing | 4248 | 2024-03-21 | 2024-03-21 09:00 | 54.7 | 127 | 81 | 8.29 | 0.92 | 13.1 | 212 | 1.63 | 0.97 | 7.39 | 1.1 | 2.3 | 22 | 4.5 | 1.05 | 6.27 | 7.73 | 158 | 0.34 | 0.25 | 7.52 | 1.21
Hydraulic Stress testing | 4248 | 2024-03-25 | 2024-03-25 11:00 | 65.3 | 182 | 66 | 17.1 | 0.895 | 23.5 | 227 | 2.67 | 1.69 | 7.55 | 0.951
Hydraulic Stress testing | 4248 | 2024-03-25 | 2024-03-25 11:25 | [11 empty] | 4.3 | 32 | 7.5 | 3.8 | 5.98 | 10.9 | 137 | 0.53 | 0.36 | 7.42 | 1.55
Hydraulic Stress testing | 4752 | 2024-03-27 | 2024-03-27 10:15 | [11 empty] | 3.1 | 26 | 8.5 | 6.12 | 4.45 | 11.6 | 175 | 0.56 | 0.4 | 7.79 | 1.61
Hydraulic Stress testing | 4752 | 2024-03-27 | 2024-03-27 10:25 | 92.8 | 270 | 262 | 15.1 | 0.895 | 23.2 | 230 | 3.15 | 1.83 | 7.66 | 2.59
Hydraulic Stress testing | 4752 | 2024-03-28 | 2024-03-28 08:00 | [11 empty] | 3.6 | 27 | 8.5 | 5.59 | 3.92 | 9.85 | 160 | 0.54 | 0.39 | 7.56 | 2.13
Hydraulic Stress testing | 4752 | 2024-03-28 | 2024-03-28 08:25 | 37.5 | 166 | 96 | 9.24 | 0.99 | 14.2 | 194 | 1.84 | 1.17 | 7.47 | 2.3

## Storm Scenario Testing
| SPOTS | [5 empty] | Feed | [10 empty] | Effluent
[7 empty] | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
| Stage | Flow (l/day) |  | Date/Time | Time | Hours after start | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l
| Storm Scenario 1 |  | 2024-04-03 | 2024-04-03 08:00 | 8:00 |  | 32.1 | 40 | 26.25 | 5.62 |  | 9.28 | 226 | 0.98 | 0.93 |  | 1.02
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 10:30 | 10:30 | 2.5 | 258 | 892 | 632 | 12.8 | 0.95 | 30.2 | 202 | 4.69 | 2.28 | 7.36 | 6.2 | 3.8 | 24 | 2.5 | 2.4 | 5.26 | 8.08 | 163 | 0.38 | 0.38 | 7.71 | 0.153
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 11:00 | 11:00 | 3 | [11 empty] | 1.8 | 24 | 4.5 | 1.43 | 5.19 | 7.4 | 157 | 0.4 | 0.34 | 7.81 | 0.773
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 11:15 | 11:15 | 3.25 | [11 empty] | 1.8 | 17 | 3 | 1 | 3.71 | 5.42 | 144 | 0.28 | 0.25 | 7.92 | 0.807
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 11:30 | 11:30 | 3.5 | [11 empty] | 1.8 | 16 | 3 | 0.69 | 3.62 | 4.91 | 148 | 0.3 | 0.24 | 7.89 | 1.07
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 11:45 | 11:45 | 3.75 | [11 empty] | 1.8 | 18 | 4 | 0.408 | 3.43 | 4.44 | 152 | 0.25 | 0.22 | 7.86 | 1.2
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 12:00 | 12:00 | 4 | [11 empty] | 1.8 | 17 | 5.5 | 0.408 | 3.39 | 4.33 | 164 | 0.25 | 0.22 | 7.87 | 1.3
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 12:30 | 12:30 | 4.5 | [11 empty] | 1.8 | 19 | 5 | 0.43 | 3.39 | 4.32 | 161 | 0.28 | 0.23 | 7.97 | 1.44
| Storm Scenario 1 | 6048 | 2024-04-03 | 2024-04-03 13:00 | 13:00 | 5 | [11 empty] | 1.8 | 18 | 6 | 0.59 | 3.39 | 4.62 | 149 | 0.29 | 0.26 | 7.98 | 1.45
| Storm Scenario 1 |  | 2024-04-04 | 2024-04-04 11:30 | 11:30 | 27.5 | [11 empty] | 2.2 | 18 | 2.5 | 0.51 | 4.69 | 5.34 | 166 | 0.25 | 0.2 | 7.77 | 0.925
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 11:00 | 11:00 |  | 41.3 | 137 | 75 | 12.5 | 1.75 | 22.6 | 221 | 2.64 | 1.88 | 7.67 | 1.89 | 1.3 | 14 | 4 | 0.408 | 2.01 | 2.75 | 165 | 0.47 | 0.26 | 8.05 | 1.14
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 11:15 | 11:15 | 0.25 | [11 empty] | 1.5 | 22 | 7.5 | 0.81 | 4.02 | 5.59 | 148 | 0.35 | 0.39 | 7.87 | 1.48
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 11:30 | 11:30 | 0.5 | [11 empty] | 1.6 | 18 | 4.5 | 0.44 | 3.02 | 4.23 | 167 | 0.49 | 0.38 | 7.92 | 1.44
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 11:45 | 11:45 | 0.75 | [11 empty] | 1.2 | 17 | 10 | 0.408 | 2.66 | 3.57 | 167 | 0.39 | 0.3 | 9.48 | 1.14
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 12:00 | 12:00 | 1 | [11 empty] | 1.5 | 21 | 7 | 0.408 | 2.51 | 3.25 | 155 | 0.35 | 0.52 | 7.95 | 1
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 13:00 | 13:00 | 2 | [11 empty] | 1.4 | 18 |  | 0.408 | 2.2 | 2.86 | 162 | 0.26 | 0.22 | 8.02 | 0.738
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 14:00 | 14:00 | 3 | [11 empty] | 1.5 | 15 | 7 | 0.408 | 1.95 | 2.86 | 168 | 0.33 | 0.29 | 8.05 | 1.32
| Storm Scenario 2 | 6048 | 2024-04-09 | 2024-04-09 15:00 | 15:00 | 4 | [11 empty] | 2.4 | 19 | 6 | 0.55 | 2.1 | 3.24 | 155 | 0.34 | 0.27 | 8 | 1.3
Comp | Storm Scenario 2 |  | 2024-04-10 | 2024-04-10 14:00 | 14:00 | 27 | [11 empty] | 2.5 | 20 | 4.5 | 1 | 2.62 | 3.47 | 182 | 0.37 | 0.29 | 7.97 | 1.19
| Storm Scenario 2 | 7920 | 2024-05-30 | 2024-05-30 11:30 | 11:30 |  | 34.3 | 201 | 6.77 | 4.61 | 7.28 | 3.73 |  |  | 2.3 | 22 | 4 | 2.3 | 22 | 4 | 0.85 | 12.5 | 13.7 | 109 | 0.96 | 0.82 | 7.52 | 1.09
| Storm Scenario 3 | 7920 | 2024-05-30 | 2024-05-30 12:00 | 12:00 | 0.5 | [8 empty] | 4.9 | 32 | 15.5 | 4.9 | 32 | 15.5 | 1.67 | 11.9 | 14.4 | 125 | 1.44 | 1.21 | 7.35 | 2.92
| Storm Scenario 3 | 7920 | 2024-05-30 | 2024-05-30 12:30 | 12:30 | 1 | [8 empty] | 5.2 | 30 | 10 | 5.2 | 30 | 10 | 1.83 | 11.7 | 15 | 128 | 1.27 | 1.06 | 7.43 | 2.57
| Storm Scenario 3 | 7920 | 2024-05-30 | 2024-05-30 13:00 | 13:00 | 1.5 | [8 empty] | 4 | 31 | 9.5 | 4 | 31 | 9.5 | 1.67 | 12.2 | 14.7 | 132 | 1.2 | 1.04 | 7.52 | 2.4
| Storm Scenario 3 | 7920 | 2024-05-30 | 2024-05-30 13:30 | 13:30 | 2 | 34.4 | 212 | 6.39 | 4.37 | 7.22 | 3.06 |  |  | 4.8 | 27 | 7.5 | 4.8 | 27 | 7.5 | 1.66 | 12.5 | 15.1 | 132 | 1.16 | 0.99 | 7.2 | 2.12
| Storm Scenario 3 | 7920 | 2024-05-30 | 2024-05-30 14:30 | 14:30 | 3 | [8 empty] | 5 | 28 | 8 | 5 | 28 | 8 | 1.63 | 12.7 | 15.4 | 113 | 1.11 | 0.95 | 7.44 | 1.78
Comp | Storm Scenario 3 |  | 2024-05-31 | 2024-05-31 13:00 | 13:00 | 25.5 | [11 empty] | 1.8 | 29 | 3 | 0.408 | 14.7 | 15.4 | 113 | 0.72 | 0.71 | 7.74 | 0.976
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 10:15 | 10:15 |  | 32.6 | 264 | 6.3 | 5.03 | 7.51 | 2.92 |  |  | 3.5 | 28 | 9 | 3.5 | 28 | 9 | 0.59 | 11 | 12.5 | 126 | 0.8 | 0.61 | 7.72 | 2.29
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 10:45 | 10:45 | 0.5 | [8 empty] | 2.2 | 20 | 17 | 2.2 | 20 | 17 | 0.408 | 8.07 | 9.62 | 114 | 1.13 | 0.62 | 7.69 | 4.3
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 11:15 | 11:15 | 1 | [8 empty] | 2.2 | 22 | 6 | 2.2 | 22 | 6 | 0.408 | 7.65 | 8.49 | 127 | 0.45 | 0.38 | 7.75 | 1.52
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 11:45 | 11:45 | 1.5 | 32.7 | 265 | 6.36 | 4.94 | 7.27 | 3.25 |  |  | 3.7 | 25 | 4 | 3.7 | 25 | 4 | 0.73 | 7.54 | 8.72 | 117 | 0.5 | 0.42 | 7.68 | 1.7
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 12:15 | 12:15 | 2 | [8 empty] | 3.8 | 23 | 7 | 3.8 | 23 | 7 | 0.97 | 7.86 | 9.18 | 140 | 0.54 | 0.47 | 7.68 | 1.62
| Storm Scenario 4 | 8496 | 2024-06-03 | 2024-06-03 13:15 | 13:15 | 3 | [8 empty] | 3.9 | 29 | 9.5 | 3.9 | 29 | 9.5 | 1.42 | 8.13 | 10.2 | 136 | 0.77 | 0.62 | 7.62 | 1.91
| Storm Scenario 5 | 8496 | 2024-06-03 | 2024-06-03 14:15 | 14:15 | 4 | [8 empty] | 6.1 | 29 | 9 | 6.1 | 29 | 9 | 1.73 | 8.2 | 11.2 | 129 | 0.82 | 0.67 | 7.71 | 1.64
Comp | Storm Scenario 5 |  | 2024-06-04 | 2024-06-04 09:00 | 9:00 | 22.75 | [11 empty] | 4.1 | 29 | 9 | 0.61 | 10.7 | 12 | 118 |  | 0.71 | 6.94
| COMPS | [5 empty] | Feed | [10 empty] | Effluent
[7 empty] | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
| Stage | Flow (l/day) |  | Date/Time |  |  | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l
| Storm Scenario 2 | 6048 | 2024-04-10 | 2024-04-10 14:00 | [13 empty] | 2.5 | 20 | 4.5 | 1 | 2.62 | 3.47 | 182 | 0.37 | 0.29 | 7.97 | 1.19
| Storm Scenario 3 | 2016 | 2024-05-31 | 2024-05-31 13:00 | [13 empty] | 1.8 | 29 | 3 | 0.408 | 14.7 | 15.4 | 113 | 0.72 | 0.71 | 7.74 | 0.976
| Storm Scenario 4 | 8496 | 2024-06-04 | 2024-06-04 09:00 | [13 empty] | 4.1 | 29 | 9 | 0.61 | 10.7 | 12 | 118 |  | 0.71 | 6.94

## P Spiked Crude Testing
SPOTS |  |  |  | Feed | [10 empty] | Effluent
|  |  |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | Notes
Phos Dosing | 2016 | 2024-05-15 | 2024-05-15 08:40 | [11 empty] | 7.3 | 64 | 10.5 | 0.64 | 7 | 9.3 | 161 | 1.73 | 1.39 | 7.6 | 4.27 | Started dosing Glazebury Crude with P
Phos Dosing | 2016 | 2024-05-15 | 2024-05-15 08:45 | 95.9 | 597 | 440 | 18.3 | 0.895 | 33.6 | 204 | 10.8 | 8.15 | 7.05 | 6.2
Phos Dosing | 2016 | 2024-05-15 | 2024-05-15 12:00 | [11 empty] | 5.8 | 62 | 11 | 0.66 | 7 | 9.1 | 155 | 1.81 | 1.46 | 7.56 | 4.41
Phos Dosing | 2016 | 2024-05-16 | 2024-05-16 11:40 | 52.3 | 189 | 88 | 24.3 | 1.02 | 37.9 | 266 | 10.5 | 9.37 | 7.34 | 1.8 | 2.8 | 56 | 8 | 0.65 | 7.16 | 9.71 | 128 | 1.84 | 1.74 | 7.72 | 3.88
Phos Dosing | 2016 | 2024-05-20 | 2024-05-20 11:30 | 94 | 351 | 220 | 29.8 | 0.895 | 42.7 | 289 | 10.8 | 9.37 | 7.29 | 4.16 | 2.1 | 33 | 5.5 | 0.408 | 4.47 | 5.47 | 157 | 0.82 | 0.67 | 8.02 | 2.6
Phos Dosing | 2016 | 2024-05-21 | 2024-05-21 13:00 | [11 empty] | 3.2 | 37 | 9 | 0.46 | 5.45 | 6.52 | 149 | 0.95 | 0.79 | 7.7 | 2.91
Phos Dosing | 2016 | 2024-05-22 | 2024-05-22 15:00 | 117 | 357 | 261 | 8.56 | 1.46 | 21.1 | 100 | 9.99 | 8.3 | 6.82 | 4.13 | 3.2 | 38 | 9.5 | 0.408 | 6.24 | 7.59 | 144 | 0.73 | 0.64 | 7.5 | 2.41
Phos Dosing | 2016 | 2024-05-23 | 2024-05-23 09:45 | 72.1 | 255 | 186 | 7.98 | 1.08 | 17.6 | 113 | 9.46 | 7.75 | 7.4 | 3.93 | 2.2 | 30 | 7.5 | 0.408 | 4.84 | 5.83 | 136 | 0.94 | 0.84 | 7.67 | 2.33
Phos Dosing | 2016 | 2024-05-23 | 2024-05-23 13:30 | 62.5 | 227 | 150 | 7.84 | 2.19 | 15 | 134 | 9.69 | 8.33 | 7.21 | 3.22 | 2.6 | 29 | 6.5 | 0.408 | 4.78 | 5.79 | 80 | 0.94 | 0.85 | 7.77 | 2.21
Phos Dosing | 2016 | 2024-05-24 | 2024-05-24 09:00 | [11 empty] | 1.9 | 32 | 10.5 | 0.408 | 4.93 | 5.7 | 118 | 1.07 | 1.01 | 7.48 | 2.14
Phos Dosing | 2016 | 2024-05-24 | 2024-05-24 12:30 | 46 | 219 | 113 | 13.1 | 2.04 | 20.8 | 199 | 9.69 | 8.69 | 7.28 | 2.05 | 1.9 | 26 | 6.5 | 0.408 | 5 | 5.68 | 108 | 1.02 | 1.01 | 7.94 | 1.9
Phos Dosing | 2016 | 2024-05-28 | 2024-05-28 12:45 | 126 | 414 | 133 | 29.1 | 0.895 | 43.8 | 252 | 11.7 | 10.2 | 7.38 | 3.13 | 2.5 | 29 | 6 | 0.408 | 2.72 | 3.74 | 120 | 0.51 | 0.43 | 8.21 | 2.47
Phos Dosing | 2016 | 2024-05-28 | 2024-05-28 14:10 | [11 empty] | 2 | 29 | 9 | 0.408 | 3.04 | 4.12 | 131 | 0.53 | 0.44 | 8.11 | 2.55
Phos Dosing | 2016 | 2024-05-29 | 2024-05-29 10:45 | 106 | 308 | 213 | 27.7 | 0.895 | 40.8 | 269 | 12 | 9.4 | 7.41 | 3.2 | 4.3 | 34 | 10 | 1.45 | 7.89 | 10.1 | 134 | 1.08 | 1 | 7.77 | 1.86
Phos Dosing | 2016 | 2024-05-29 | 2024-05-29 13:45 | 121 | 368 | 240 | 29.8 | 0.895 | 43 | 266 | 10.4 | 8.43 | 7.46 | 3.21 | 2.5 | 27 | 5.5 | 1.1 | 8.61 | 10.2 | 115 | 0.96 | 0.87 | 7.76 | 1.49 | Stopped dosing Glazebury Crude with P
COMPS |  |  |  | Feed | [10 empty] | Effluent
|  |  |  | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON | BOD | COD | SOLI | AMMO | NTOX | TONI | ALKA | PHOS | ORPH | PH | IRON
Stage | Flow (l/day) |  | Date/Time | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ALKA | mg/l | mg/l | pH units | mg/l | Notes
Phos Dosing | 2016 | 2024-05-14 | 2024-05-14 10:00 | 80 | 253 | 101 | 36.1 | 0.895 | 43.9 | 291 | 5.45 | 3.96 | 7.72 | 1.28 | 8.4 | 94 | 11 | 1.08 | 10.5 | 13.7 | 195 | 1.5 | 1.1 | 7.52 | 3.36 | Started dosing Glazebury Crude with P
Phos Dosing | 2016 | 2024-05-15 | 2024-05-15 08:30 | [11 empty] | 7.4 | 71 | 12 | 0.49 | 7.94 | 9.99 | 172 | 1.55 | 1.18 | 7.59 | 3.81
Phos Dosing | 2016 | 2024-05-15 | 2024-05-15 08:40 | 89.6 | 501 | 345 | 18.3 | 1.79 | 32 | 190 | 10.7 | 8.16 | 6.83 | 5.47
Phos Dosing | 2016 | 2024-05-16 | 2024-05-16 10:00 | 56 | 293 | 88 | 17.6 | 0.895 | 30.5 | 179 | 9.07 | 7.53 | 7.23 | 3.85 | 4.1 | 65 | 10 | 0.55 | 7.08 | 9.75 | 153 | 1.69 | 1.48 | 7.74 | 3.86
Phos Dosing | 2016 | 2024-05-17 | 2024-05-17 08:00 | 70 | 109 | 31 | 27.9 | 0.895 | 35.6 | 279 | 9.55 | 9.14 | 7.36 | 1.1 | 3.2 | 43 | 8.5 | 0.71 | 10.3 | 14.1 | 135 | 1.89 | 1.67 | 7.6 | 3.44
Phos Dosing | 2016 | 2024-05-17 | 2024-05-17 12:05 | [11 empty] | 3.2 | 52 | 8.5 | 0.49 | 8.71 | 12.8 | 148 | 1.84 | 1.66 | 7.6 | 3.72
Phos Dosing | 2016 | 2024-05-21 | 2024-05-21 09:30 | 86.5 |  | 432 | 0.693 | 5.45 | 37.6 | 322 | 9.56 | 0.85 | 7.55 | 2.17 | 3.2 | 39 | 13.5 | 0.408 | 5.26 | 6.92 | 154 | 1.08 | 0.89 | 7.75 | 3.13
Phos Dosing | 2016 | 2024-05-22 | 2024-05-22 10:00 | 250 | 820 | 616 | 21.8 | 1.79 | 41 | 176 | 8.28 | 5.36 | 6.99 | 5.54 | 3.2 | 42 | 20 | 0.408 | 6.25 | 7.8 | 159 | 1.29 | 0.91 | 7.29 | 4.42
Phos Dosing | 2016 | 2024-05-23 | 2024-05-23 10:00 | 87.4 | 270 | 179 | 8.04 | 0.895 | 17.2 | 110 | 9.68 | 7.74 | 7.3 | 4.09 | 5.9 | 40 | 21.5 | 0.408 | 5.4 | 7.28 | 144 | 1.43 | 1.2 | 7.69 | 5.06
Phos Dosing | 2016 | 2024-05-24 | 2024-05-24 09:00 | 55.2 | 114 | 115 | 7.48 | 2.12 | 13.8 | 129 | 7.93 | 7.48 | 7.32 | 1.3
Phos Dosing | 2016 | 2024-05-24 | 2024-05-24 09:01 | [11 empty] | 2.1 | 34 | 9 | 0.75 | 4.93 | 5.47 | 121 | 0.92 | 0.92 | 7.7 | 1.93
Phos Dosing | 2016 | 2024-05-28 | 2024-05-28 09:00 | 37.8 | 180 | 125 | 16.1 | 0.895 | 25 | 195 | 10.8 | 9.41 | 7.65 | 3.07 | 3.4 | 38 | 19.5 | 0.408 | 3.2 | 4.73 | 138 | 1.08 | 1.16 | 8.88 | 2.74
Phos Dosing | 2016 | 2024-05-29 | 2024-05-29 09:00 | 101 | 336 | 220 | 27.7 | 0.895 | 40.6 | 257 | 11.5 | 9.47 | 7.65 | 2.91 | 2.7 | 34 | 10.5 | 0.8 | 5.29 | 6.51 | 137 | 0.89 | 0.78 | 7.65 | 2.37 | Stopped dosing Glazebury Crude with P