## Job comments
Date | Job comments
2023-07-09 | Pre-site Job notes state flooding from m/h in the road. Pics uploaded from customer showing flooding coming from chamber 6200. No historical issues at the prop and no hydraulic issues reported in INS on the post code provided. Searched for hydraulic issues on post code but again none in INS. We have a DNM monitor in combined chamber 6200. Checked the aqua DNA, No alerts triggered but checked the platform and it does show a spike in flows from last night. Arrived onsite, witnessed dry tissue around chamber 6200. Also witnessed rag around h/w gully in the road. Lifted 6200 this was now clear and flowing but evident it had been surcharged, rag all around stepping irons and the monitor. Traced d/s lifting chamber 6302 this was clear with no evidence of being surcharged. Carried out litter pick of minor rag that had spilled from chamber 6200 and the h/w gully. FW’s raised for CCTV d/s from 6200 for approx 230m into chamber 5302. Suspect this may have flooded due to too much rainfall coming into chamber 6200 then taking a sharp bend which may have restricted the flow causing the flooding. Coded as hydraulic flooding for now until CCTV complete.